## DS SS DNS (hidden)
警告代码 | 警告信息 | 解释 | 报错代码 | 报错信息 | 解释 | 自检顺序
1 | 逆变电流突变过大 | 如果相邻的IO(1)和IO(2)差值过大，说明逆变器异常导致输出电流波形畸变，需要快速保护逆变器 保护方案：重追 | 1 | GFCI设备报错 | 此设备实际是电流传感器，用于检测漏电流（IL+IN）。逆变器自检时,第3个步骤就是对此设备进行测试，确认是否正常。如果异常，则保错
2 | 电网电压保护 | 电网电压的瞬时值超过设定的上限（过压），需要快速保护逆变器。通常可能会由以下几种触发： (1)电网断开瞬间，电压被迅速拉升； (2)大型设备启/停，导致电网瞬间突变 (3)电网电压采样电路异常； 保护方案：重连 | 2 | HCT设备报错 | 此设备是逆变电流传感器，逆变器自检时，第2个步骤就是对此设备进行测试，确认是否正常。如果异常，则保错
4 | 逆变过流（软件保护） | 软件检测，电网电流的瞬时值（如图中的点IO(2)）超过设定的上限，需要快速保护逆变器，否则可能导致逆变炸机。通常可能会由以下几种触发： (1)AC高阻抗导致电流震荡。 (2)大型设备启/停，导致电网瞬间突变，进而引起电流突变 (3)功率突降导致Bus低于电网电压 保护方案：重追 | 4 | REF电压报错 | N/A
8 | Pv1电流保护（软件保护） | PV电流的AD采样值超过设定的上限，需要快速保护逆变器，否则可能导致Boost炸机。通常可能会由以下几种触发： (1)DC高阻抗导致电流震荡。 保护方案：重连 | 8 | Consistent DCI fault | N/A
16 | Pv2电流保护（软件保护） |  | 16 | Consistent GFCI fault | 主DSP检测的电网频率和副DSP检测结果差值大于100mA
32 | Bus电压过高 | 并网时，理想状态是控制母线电容的电压 = Vac*1.414+35V。如果因异常情况导致此电压超过保护值（超过母线电容耐压值），会导致电容损坏。通常可能会由以下几种触发： (1)PV侧功率突增。 (2)AC输出功率被限制。 保护方案：重连 | 32 | Bus电压过低 | N/A（如果bus电压过低，会重连，产生warningcode，不会报错误信息）
64 | 锁相错误 | (1)DSP会根据算法计算出电网电压当前相位； (2)硬件会提供一个相位结果（过零点翻转信号）； 逆变器在自检/重追时会比较这2个结果，如果差值较大，则报锁相异常。 保护方案：重连 | 64 | Bus电压过高 | N/A（bus电压过高，实际是报2048错误信息）
128 | 逆变过流（硬件保护） | 硬件实现，电网电流的瞬时值（如图中的点IO(2)）超过设定的上限，需要快速保护逆变器，否则可能导致逆变炸机。通常可能会由以下几种触发： (1)AC高阻抗导致电流震荡。 (2)大型设备启/停，导致电网瞬间突变，进而引起电流突变 (3)功率突降导致Bus低于电网电压 保护方案：硬件封驱动，并通知DSP重追 | 128 | Device fault | 逆变器报错，但错误类型是未知的（不在此错误列表中）
256 | PV1电流限制 | PV电流的AD采样值超过设定的上限，需要快速保护逆变器，否则可能导致Boost炸机。通常可能会由以下几种触发： (1)DC高阻抗导致电流震荡。 保护方案：重连 | 256 | Bus soft timeout | N/A
512 | 快速断电保护 | 连续3个电网周期检测不到电网，才报电网丢失。在此3个周期内会继续并网打驱动。如果此时AC侧存在变压器（比如台湾），逆变电流会失控，比较容易导致逆变炸机。因此，增加此保护 保护方案：重连 | 512 | 市电丢失 | 连续3个电网周期没有检测到电网过零点，则认为电网丢失
1024 | Bus电压低 | 电流由高电压流向低电压。母线电容电压过低，会导致电网向逆变器反馈能量，导致逆变过流，严重时导致逆变炸机。通常可能会由以下几种触发： (1)DC侧能量不够（早晨起机） (2)功率突降； (3)硬件异常，无法实现升压功能。 保护方案：重连 | 1024 | GFCI fault | 漏电流（IL+IN）超过30mA/60mA/150mA/300mA要停止并网。漏电流主要有以下产生原因： (1)PV面板对地存在寄生电容，使得部分电流从此回路流到大地，产生漏电流；面板使用越久，此漏电流越大 (2)人体触电。电流通过人体留到大地 (3)逆变器元器件损坏
2048 | PV 电压低 | 主要出现在早晨/傍晚 保护方案：重连 | 2048 | Bus电压过高 | 并网时，理想状态是控制母线电容的电压 = Vac*1.414+35V。如果因异常情况导致此电压超过保护值（超过母线电容耐压值），会导致电容损坏。通常可能会由以下几种触发： (1)PV侧功率突增。 (2)AC输出功率被限制。
4096 | Bus软启动失败 | 逆变器自检时，如果PV电压较低，则会先抬升Bus电压= Vac*1.414+50V。避免并网时出现Bus电压过低保护。 保护方案：重连 | 4096 | 逆变电流Hwover | N/A
8192 | AC电压电流相位差大 | 已取消 | 8192 | 过温 | 逆变器内部温度过高，会影响元器件的寿命。因此超过阈值（DNS/DS/NS 85°），需报错保护
16384 | Bus电压瞬时值过低 | 并网时，实时检测电网电压，避免出现Bus电压过低，导致逆变过流现象。 保护方案：重连 | 16384 | Auto Test fault | N/A
32768 | Relay检测时Bus电压低 | relay自检结束后，就会并网发电。此检测意义是，在并网前再次确认Bus电压是否满足并网条件，避免出现bus过压，导致逆变过流现象。 保护方案：重连 | 32768 | Pv ov fault | PV输入电压过高（超过输入侧元器件的耐压规格），会损坏元器件
|  |  | 65536 | Fan fault | 逆变器自检过程中，全速运转风扇，并检测转速，如果实际转速低于50%，则认为风扇异常，报错。
|  |  | 131072 | 电网电压报错
|  |  | 262144 | ISO failure | PV端子和大地的阻抗理论值是无穷大，如果偏小会导致漏电流，甚至逆变炸机。各机种阈值为XS 150K;NS 50K;DNS 50K；DS 150K
|  |  | 524288 | DCI超出范围 | 电网中的直流分量过大会导致电网系统的变压器饱和；增加电网电缆的腐蚀；还可能增加谐波分量，降低电网质量。因此，并网后，需实时检测输出电流的直流分量，如果大于阈值（法规要求为额定电流*0.5%），需报错
|  |  | 1048576 | ConsistentVFFault | N/A
|  |  | 2097152 | ConsistentFault | N/A
|  |  | 4194304 | ConsistentFreqFault | 主DSP检测的电网频率和副DSP检测结果差值大于1Hz
|  |  | 8388608 | ConsistentVoltFault | 主DSP检测的电网电压和副DSP检测结果差值大于30V
|  |  | 16777216 | RelayFailure | N/A
|  |  | 33554432 | Relay check failure | 输出侧的继电器无法吸合/断开。
|  |  | 67108864 | HCT Failure | N/A
|  |  | 134217728 | GFCI Device Failure | N/A
|  |  | 268435456 | MS Version Fault | N/A
|  |  | 536870912 | GridFreqFault | 电网频率异常
|  |  | 1073741824 | EepronRwFault | 用于存储发电量、等数据的元件(类似手机的SD卡)损坏，导致读/写数据失败
|  |  | 2147483648 | SPI Failure | 主副DSP之间的通讯异常

## NS (hidden)
警告代码 | 警告信息 | 解释 | 报错代码 | 报错信息 | 解释
1 | 逆变电流突变过大 |  | 1 | GFCI Failure
2 | 电网电压保护 |  | 2 | AC HCT Failure
4 | 逆变过流（软件保护） |  | 4 | NA
8 | Pv电流保护 |  | 8 | NA
16 | Pv电压保护 |  | 16 | 漏电流主副CPU一致性检测错误
32 | Bus电压过高 |  | 32 | NA
64 | DCI limit |  | 64 | DC Bus High
128 | 逆变过流（硬件保护） |  | 128 | NA
256 | Boost过流（硬件保护） |  | 256 | NA
512 | NA |  | 512 | Utility loss
1024 | Bus电压低 |  | 1024 | Ground I Failure
2048 | PV 电压低 |  | 2048 | Bus高压保护
4096 | Bus软启动失败 |  | 4096 | NA
8192 | NA |  | 8192 | Over Temperature
16384 | NA |  | 16384 | NA
32768 | Relay检测时Bus电压低 |  | 32768 | Pv over voltage
|  |  | 65536 | NA
|  |  | 131072 | 主CPU检测电网电压报错
|  |  | 262144 | ISO failure
|  |  | 524288 | DCI high
|  |  | 1048576 | 电网电压主副CPU一致性检测错误
|  |  | 2097152 | NA
|  |  | 4194304 | 电网频率主副CPU一致性检测错误
|  |  | 8388608 | 电网电压主副CPU一致性检测错误
|  |  | 16777216 | NA
|  |  | 33554432 | 继电器检测异常
|  |  | 67108864 | NA
|  |  | 134217728 | NA
|  |  | 268435456 | NA
|  |  | 536870912 | 电网频率异常
|  |  | 1073741824 | Eeprom R/W Failure
|  |  | 2147483648 | SPI Failure

## MT (hidden)
报错代码 | 报错信息 | 解释
32768 | 驱动异常(Check中自检，未用)
16384 | 硬件故障(TZ被触发，但未识别到触发源)
8192 | 逆变驱动错误(I型过压,T型直通)
4096 | 逆变电流反向
2048 | PV异常（PV电压从NC到OK，或者OK到NC）
1024 | 逆变硬件过流
512 | PV软件过流
256 | PV硬件过流
128 | Bus电压低
64 | 逆变软件过流
32 | 逆变失控(输出电流跟不上环路电流给定增大)
16 | Bus不平衡
8 | Pll锁相失败
4 | PV电压低
2 | 光耦保护
1 | 逆变电流不平衡

## 重点问题 (hidden)
序号 | 机型分类 | 常见报错 | 警告代码 | 报错代码 | 元件在机体内的功能（没有则无） | 故障原理 | 如何判定 | 有效解决方案 | 其他
1 | DS SS DNS | GFCI设备报错 |  | 1 | 电流传感器，用于检测漏电流; | 在逆变器自检时检测1次，分2步： 步骤1：无AC输出电流，传感器的检测结果理论上应该是0，如果大于阈值，则说明零漂过大，需报错； 步骤2：硬件强行提供50mA漏电流，传感器的检测结果理论上应该是50mA，如果超出范围，则说明精度较差，需报错； | 1、机器报错，5S后重新自检；单相连续3次后重启SPS；三相连续3次则一直报错 2、LCD显示：残余电流自检异常/GFCI Fail 3、监控数据的错误信息； | (1)排线松动:检查/更换排线； (2)传感器异常:更换控制板/输出板。如果还是报错，则返厂维修/换机
2 |  | HCT设备报错 |  | 2 | 电流传感器，用于检测输出侧电流 | 仅逆变器自检时检测1次： 无AC输出电流，传感器的检测结果理论上应该是0，如果检测出电流且大于阈值，则说明零漂过大，需报错； | 1、机器报错，5S后会重新自检；连续3次后重启SPS；三相连续3次则一直报错 2、LCD显示：输出电流传感器异常/AC HCT Fail 3、监控数据； | (1)排线松动:检查/更换排线； (2)传感器异常:更换控制板/输出板。如果还是报错，则返厂维修/换机
3 |  | Bus电压过低 |  | 32 | 已取消此错误信息（如果bus电压过低，则重连，产生warningcode）
4 |  | Bus电压过高 |  | 64 | N/A(和错误代码64一致)
5 |  | Device fault |  | 128 | 无 | 逆变器报错，但错误类型不在信息列表中 | 1、LCD显示：自检异常/Device Fail 2、监控数据
6 |  | Bus电压过高 |  | 2048 |  | 逆变器并网，且boost工作情况下，并网时，理想状态是将母线电容的电压 稳定在 Vac*1.414+35V。Bus电压（20ms平均值）因为异常导致大于保护阈值（默认DNS600V/NS500V）则报错。可能带来的风险： (1)导致母线电容损坏 (2)降低逆变器效率 | 1、机器报错，LCD显示：直流母线电压过高/DC Bus High 2、监控数据（错误信息+Bus电压） 3、多次报错后，可正常并网； | (1)PV侧功率突增：可不处理 (2)AC输出功率被限制（比如澳洲缓慢加载、防逆流、DRED）：关闭输出限值功能。 (3)Bus电压采样电路损坏：实测bus电压和监控数据做对比。如果差异过大，返厂维修。 (4)逆变损坏，功率无法输出：检测逆变驱动。如果损坏，返厂维修。
7 |  | DCI超出范围 |  | 524288 | 无 | 并网实时检测：AC输出电流中的直流分量超过限制限制（一般是1A），则报错。DCI过高带来的风险有： (1)导致电网系统的变压器饱和； (2)增加电网电缆的腐蚀； (3)增加谐波分量，降低电网质量。 | 1、逆变器报错，5S后会重新自检； 2、LCD显示：输出直流分量过高保护/DCI High 3、监控数据； | (1)法规限值偏小（比如意大利、巴西）：软件升级，修改限值 (2)排线否松动：检查/更换排线 (3)AC电流传感器损坏：更换控制板/输出板。如果还是报错，返厂维修
8 |  | Relay Failure |  | 16777216 | 已取消此错误检测
9 |  | Relay check failure |  | 33554432 | 用于断开/闭合电网 | 在逆变器自检时检测1次，分2步： 步骤1：relay断开时，2端压差理论上应该是很大。如果小于阈值，则认为relay粘死，报错； 步骤2：relay吸合时，2端压差理论上应该是0。如果大于阈值，则认为relay无法吸合，报错； | 1、逆变器报错，5S后会重新自检；连续3次重启SPS 2、LCD显示：继电器检测异常/Relay Check Fail 3、监控数据； | (1)零线带电： (2)排线松动：检测/更换排线 (3)relay驱动电压不够：升级最新程序； (4)relay 损坏:更换输出板/返回维修
10 |  | GFCI Device Failure |  | 134217728 | 已取消此错误检测
11 |  | HCT Failure |  | 67108864 | 已取消此错误检测
12 | NS | 逆变电流突变过大 | 1 |  |  | 如果相邻的IO(1)和IO(2)差值超过阈值(10A)，说明逆变器异常导致输出电流波形畸变，需要快速保护逆变器 | (1)重追 (2)warningcode | 可能原因： (1)AC高阻抗导致电流震荡。 (2)大型设备启/停，导致电网瞬间突变，进而引起电流突变 (3)功率突降导致Bus低于电网电压 解决方案：确认客户现场电网质量，尝试软件升级
13 |  | 逆变过流（软件保护） | 4 |  |  | 软件检测，电网电流的瞬时值（如图中的点IO(2)）超过软件设定的上限，需要快速保护逆变器，否则可能导致逆变炸机。 | (1)重追 (2)warningcode
14 |  | Pv电流保护 | 8 |  |  | 此为软件保护。PV电流瞬时值过大，超过软件设定的上限，需要快速保护逆变器，否则可能导致Boost炸机。 | (1)重连 (2)warningcode | (1)DC高阻抗:升级程序 (2)Boost损坏：检测升压IGBT是否损坏。返厂维修
15 |  | Pv电压保护 | 16 |  |  | 此为软件保护。PV电压瞬时值过大，超过软件设定的上限，需要快速保护逆变器，否则可能导致Boost炸机。 | (1)重连 (2)warningcode | (1)PV侧面板超配：建议 (2)PV电压采样电路异常：实测PV电压和LCD显示，如果差异过大，可使用校正工具进行校正 (3)上述均无法解决，则返厂维修
16 |  | Bus电压过高 | 32 |  |  | Bus电压AD值（瞬时值，默认DNS605/NS510V）大于设定值，则认为Bus过高.具体风险，详见DNS BUS过压报错 | (1)重连 (2)warningcode | 和DNS Bus过压报错解决方案一致
17 |  | Bus电压低 | 1024 |  |  | 电流由高电压流向低电压。母线电容电压过低，会导致电网向逆变器反馈能量，触发逆变过流保护，严重时导致逆变炸机。 | (1)重连 (2)warningcode | (1)DC侧能量不够（早晨起机）:调高自检电压； (2)功率突降：无需处理； (3)AC电压过高：升级程序； (4)硬件异常：检测升压IGBT是否损坏。返厂维修
18 |  | PV 电压低 | 2048 |  |  | PV电压小于阈值（NS:自检70V/normal65V；DNS:75V；） | (1)重连 (2)warningcode (3)PV电压（实际电压+LCD显示电压） | (1)PV面板在早晨/傍晚能量较低:无需处理； (2)PV电压采样异常：检测实际电压和PV电压差值，过大则返厂维修
19 |  | Bus软启动失败 | 4096 |  |  | 逆变器自检时，如果PV电压较低，则会先抬升Bus电压= Vac*1.414+50V。避免并网时出现Bus电压过低，逆变过流。 | (1)重连 (2)warningcode | (1)PV面板在早晨/傍晚能量较低：无需处理 (2)Boost硬件电路损坏：返厂维修
20 |  | Relay检测时Bus电压低 | 32768 |  |  | relay自检结束后，就会并网发电。此检测意义是，在并网前再次确认Bus电压是否满足并网条件，避免出现bus过压，导致逆变过流现象。 | (1)重连 (2)warningcode | (1)Boost硬件电路损坏:检测升压IGBT是否异常。重启无法解决，建议返厂维修
21 | DT SDT | 逆变电流不平衡 | 1 |  |  | 理想的三相电流有效值应该是相等的。如果差值大于阈值（Iac总/2），则认为是输出电流不平衡。 | (1)重连 (2)warningcode | 1) 检查电网不平衡度： 2）逆变器电路损坏：检测逆变IGBT，返厂维修
22 |  | SPI Failure | 2 |  | N/A | N/A | N/A | N/A
23 |  | Bus不平衡 | 16 |  |  | 逆变电路采用的是T型三电平拓扑。此电路的特性是，并网后会对电容进行充电和放电，造成中点电位不停的变化。如果上下电压差值较大，会造成： (1)低次谐波变差； (2)偏高的那路电容的使用寿命缩短，甚至损坏； | (1)重连 (2)warningcode | 1）PV电压过高：检查输入电压 2）设置无功：检查是否设置无功功率、QU曲线 3）逆变器损坏：检查逆变驱动，返厂维修
24 |  | PV电流超限HW | 256 |  |  | PV电流瞬时值过大，超过硬件设定的上限，需要快速保护逆变器，否则可能导致Boost炸机。 | (1)重连 (2)warningcode | (1)DC高阻抗:升级程序 (2)PV侧输入电流过大（MT） (3)Boost损坏：检测升压IGBT是否损坏。返厂维修
25 |  | PV电流超限SW | 512 |  |  | PV电流的AD采样值（瞬时值）过大，超过软件设定的上限，需要快速保护逆变器，否则可能导致Boost炸机。 | (1)重连 (2)warningcode
26 |  | Bus Out of Control | 2048 |  |  | DT:N/A SDT:重追后，500ms再次发生重追 | (1)重连 (2)warningcode
27 |  | PV 电压低 | 4 |  |  | PV电压小于阈值（自检电压-33V，默认DT 247V；SDT 177V） | (1)重连 (2)warningcode (3)PV电压（实际电压+LCD显示电压） | (1)PV面板在早晨/傍晚能量较低:无需处理； (2)PV电压采样异常：检测实际电压和PV电压差值，过大则返厂维修
28 |  | 逆变电流超限SW | 64 |  |  | 软件检测，电网电流的瞬时值（如图中的点IO(2)）超过软件设定的上限，需要快速保护逆变器，否则可能导致逆变炸机。 | (1)重追 (2)warningcode | 可能原因： (1)AC高阻抗导致电流震荡。 (2)大型设备启/停，导致电网瞬间突变，进而引起电流突变 (3)功率突降导致Bus低于电网电压 解决方案：确认现场电网质量，尝试升级程序
29 |  | 逆变电流超限HW | 1024 |  |  | 软件检测，电网电流的瞬时值（如图中的点IO(2)）超过硬件设定的上限，需要快速保护逆变器，否则可能导致逆变炸机。 | (1)重追 (2)warningcode
30 | MT | 驱动异常(Check中自检，未用) | 32768 |  | N/A（逆变器自检时，会进行逆变驱动检测，强行打逆变驱动，产生RST三相电压。此时RST三相电压之间差值较大，则认为异常）
31 |  | 逆变电流反向 | 4096 |  |  | R/S/T中，任意一项的电压和电流反向。 | (1)重追 (2)warningcode | 是否设置PF、QU曲线
32 |  | PV异常（PV电压从NC到OK，或者OK到NC） | 2048 |  |  | 并网时，PV输入状态发生变化 |  | (1)PV接线松动：检查PV侧接线是否良好 (2)Boost硬件损坏：检查升压IGBT。返厂维修
33 |  | 逆变硬件过流 | 1024 |  | 详见DT/SDT说明
34 |  | PV软件过流 | 512 |  | 详见DT/SDT说明 | 详见DT/SDT说明
35 |  | PV硬件过流 | 256 |  | 详见DT/SDT说明
36 |  | Bus电压低 | 128 |  | 详见NS(1024)
37 |  | 逆变软件过流 | 64 |  | 详见DT/SDT说明
38 |  | 逆变失控 | 32 |  |  | 输出电流跟不上环路电流给定增大 |  | 电网突降：升级程序
39 |  | Bus不平衡 | 16 |  | 详见DT/SDT说明
40 |  | PV电压低 | 4 |  | 详见DT/SDT说明
41 |  | 光耦保护 | 2 |  |  | 硬件光耦检测到上下桥臂都是驱动 |  | 检测逆变电路是否损坏，如损坏，返厂维修；如正常，重新并网OK，则不需处理
42 |  | 逆变电流不平衡 | 1 |  | 详见DT/SDT说明
43
44
45
46
47
48
49
50
51
52
重点问题：
1. 需要对前面整理的DS SS DNS / NS/ SDT / MT机型的报错信息进行解释。
2. 对现场及400遇到的常见故障问题及代码进行详细原理解释及方案解决。（如下,，若有重复或同类型故障，可解释一次）

## Index
Index of Goodwe Trouble-Shooting Guide
Please note that the following information might be needed before starting the Trouble-shooting steps, please try to collect this information in advance including a). Inverter serial number, e.g. 95048ESU193***** b). Software version number, e.g. 171709. c). Installation date, failure date d). Frequency of failure occurrence e). Battery type f). type of backup load g). Basic installation information and site description (surrounding environment) h). Grid condition (Stable or Not) i). Weather (average temperature of the recent week) It is best to have pictures and videos as reference, which can also help analyze the problem. Detailed information needed please refer to 'Hybird inverter RMA report'.
Symptom
•BMS Comm.failure | •PV overvoltage
•Meter Comm.failure | •DC overvoltage
•Abnormal battery charging | •EEP ROM
•Abnormal battery discharging | •SPI
•Low generation | •DC bus high
•Ternimal Bunrt | •AC HCT
•Water in | •All LED on
•Cannot start | •All LED off
•ISO failure | •Waiting
•Ground I failure | •Reconnecting
•DC Injection high | •Noise
•Relay check failure
•VAC Failure
•FAC

## BMS Comm.failure
Symptom | BMS communication failure (only for lithium battery)
Fault Description | Lithium battery and inverter cannot communicate
No. | Description of Troubleshooting | Tools | Preparation before checking | Detection method | Judgment and Solution
Step 1 | BMS communication cable failure: confirm the battery communication mode is CAN or RS485 | Installation manual,meter tester | NA | Visually | Confirm that the BMS communication cable sequence is correct according to the installation manual,and the connection is normal (use the meter tester to measure the connection).
Step 2 | The battery selection is not consistent with the reality: check the battery selection through the PVmaster setting interface or read the protocol code on remote control interface(GM) then compare with the Decode table, and check whether the selection is correct | NA | Power on inverter | Visually | Turn on the inverter, connect to the PVmaster locally or connect inverter to SEMS to remotely check the communication protocol through GM to ensure that the protocol is consistent with the battery series.
Step 3 | If it is ET with BYD high-voltage battery, maybe it is not configured with battery WIFI selection: If it is ET and is equipped with BYD high-voltage battery, and there is a communication problem, it may be that the battery is not connected to the WIFI to do the inverter selection configuration. The battery software version of BYD (Battery box HV) should be higher than V3.012R. | NA | Power on inverter | Visually | Installer need to connect BYD's wifi and log in to its webpage to configure the number of battery cells and inverter manufacturers, as well as the communication protocol. Detials please refer to BYD high voltage battery installation guide.
Step 4 | Battery internal fault | Multimeter | Power on battery | Visually | Turn on the battery, measure the output voltage of the battery by using a multimeter(inverter side) to see if the output voltage of the battery is normal. Make sure that the positive and negative poles of the battery are connected to the inverter correctly.
Step 5 | This check item is only for ET: battery power cable polarity is reversed | Multimeter | Power on battery | Visually | Check and confirm the positive and negative poles of the battery power cable are not reversed to the inverter. Note: ET has polarity protection for high-voltage batteries, but not for low-voltage battery inverters. Reversed battery connection can damage the inverter.
Step 6 | This check item is mainly for Alpha-ESS Battery: the inverter should be the active version, but the actual shipment is the passive version | Calibration tool | Power on inverter | Visually | If the inverter is not connected with GOODWE SEMS, installer can use the calibration tool to modify the active mode with Laptop; if inverter is connected with SEMS, it can be modified remotely through GM by service engineers of Goodwe.
Step 7 | Inverter BMS communication port failure | NA | NA | Visually | If the above 6 steps are all normal, it might be the cause of the inverter BMS port, please contact Goodwin service team.

## Meter Comm.failure
Symptom | Meter Communication Failure
Fault Description | The meter and the inverter cannot communicate
No. | Description of Troubleshooting | Tools | Preparation before checking | Detection method | Judgment and Solution
Step 1 | Confirm the communication sequence of the meter | Installation manual, meter tester | NA | Visually | Confirm the meter communication cable sequence is correct according to the installation manual,and the connection is normal.
Step 2 | Confliction with BMS communication cable | NA | Power on Inverter | Visually | If the meter communication will return to normal after the BMS cable is unplugged, means the BMS cable need to be modified,only the CAN-H CAN-L are supposed to be kept.
Step 3 | The meter model and the inverter does not match each other | NA | NA | Visually | Replace it with Goodway smartmeter if the meter model is Ancrel three-phase meter DTSD1352
Step 4 | This check item is mainly for Alpha-ESS : the inverter should be the active version, but the actual shipment is the passive version | Calibration tool | Power on Inverter | Visually | If the inverter is not connected with GOODWE SEMS, installer can use the calibration tool to modify the active mode with Laptop; if inverter is connected with SEMS, it can be modified remotely through GM by service engineers of Goodwe.
Step 5 | Problem is with the meter itself | NA | NA | Visually | Replace the meter*
Step 6 | Inverter meter communication port failure | NA | NA | Visually | If the above 5 steps are all normal, it might be the cause of the inverter, please contact Goodwin service team.

## Abnormal battery charging
Symptom | Abnormal battery charging
Fault Description | The battery fails to be charged or isn't charged at normal power
No. | Description of Troubleshooting | Tools | Preparation | Detection method | Judgment and Solution
Step 1 | BMS communication is abnormal: check the BMS fault code | NA | Power on inverter | Visually | Handle it according to BMS communication failure solutions.
Step 2 | PV master charging current has set the limit: check whether to set the upper limit of charging current through the advanced settings of PV master | NA | Power on inverter | Visually | Modify through PV master or remote control interface.
Step 3 | If it is Lead-acid battery,there maybe capacity limit: check the battery capacity setting, charging current = battery capacity * 0.15 | NA | Power on inverter | Visually | Set according to the actual battery capacity
Step 4 | BMS charging current limit: check BMS charging current limit through monitoring data of PVmaster | NA | Power on inverter | Visually | Explain to the customer that BMS charging current limit, no need to deal with.
Step 5 | The battery is full: check the battery SOC, check whether the battery BMS alarm has charging overvoltage | NA | Power on inverter | Visually | Explain to the customer that the battery is fully charged and does not require disposal.
Step 6 | Abnormal communication of the meter: check the communication status of the meter | NA | Power on inverter | Visually | Handle it according to meter communciation failure solutions.
Step 7 | Work mode setting: confirm whether the inverter is set to the economic mode, and charge and discharge according to the user setting value in the economic mode | NA | Power on inverter | Visually | Modify the mode setting through PV master or remote control.
Step 8 | The safety curve setting may affect the charging: confirm the safety curve setting of the inverter, and check whether the current inverter's grid voltage and frequency and other parameters trigger the curve | NA | Power on inverter | Visually | No need to deal with or close the safety curve (according to local requirements)
Step 9 | If the PV voltage is too high, the battery may not be charged | NA | NA | Visually | Reduce the number of strings, so that the PV voltage of the machine is reduced to the normal range.
Step 10 | Inverter cause | NA | NA | Visually | If the above 9 steps are all normal, contact Goodwe service team.

## Anmormal battery discharging
Symptom | Abnormal battery discharging
Fault Description | The battery fails to be discharged or isn't discharged at normal power
No. | Description of Troubleshooting | Tools | Preparation | Detection method | Judgment and Solution
Step 1 | BMS communication is abnormal: check the BMS fault code | NA | Power on inverter | Visually | Handle it according to BMS communication failure solutions.
Step 2 | PV master discharging current has set the limit: check whether to set the upper limit of discharging current through the advanced settings of PV master | NA | Power on inverter | Visually | Modify through PV master or remote control interface.
Step 3 | BMS discharge current limit: Check the BMS discharge current limit through monitoring data or PV master | NA | Power on inverter | Visually | Explain to the customer no need to deal with
Step 4 | Battery DOD protection: view battery SOC, PVmaster or remotely to see if battery reachs the DOD protection value | NA | Power on inverter | Visually | Explain to the customer no need to deal with
Step 5 | Battery forced charging: check if BMS sends a charging command (diagnostic code) | NA | Power on inverter | Visually | Explain to the customer no need to deal with
Step 6 | Abnormal communication of the meter: check the communication status of the meter | NA | Power on inverter | Visually | Handle according to the meter communication failure solutions.
Step 7 | Anti-reverse setting: PVmaster or remotely confirm whether the inverter is in anti-reverse mode | NA | Power on inverter | Visually | Explain to the customer no need to deal with
Step 8 | Inverter mode setting: confirm whether the inverter is set to the economic mode, and charge and discharge according to the user setting value in the economic mode | NA | Power on inverter | Visually | Modify the mode setting through PV master or GM remote control.
Step 9 | Safety curve setting: confirm the safety curve setting of the inverter, and check whether the parameters such as the grid voltage and frequency of the current inverter trigger the curve | NA | Power on inverter | Visually | There is no need to deal with or closse the safety curve (according to local requirements).
Step 10 | If the PV voltage is too high, the battery may not be discharged | NA | NA | Visually | Reduce the number of strings, so that the PV voltage of the inverter is reduced to the normal range.
Step 11 | Inverter cause | NA | NA | Visually | If the above 10 steps are all normal, contact Goodwe service team.

## Low Generation
Symptom | Low generation
Fault Explanation | Generation does not achieve the expected results
No. | Description of Troubleshooting | Tools | Preparation | Detection method | Judgment and Solution
Step 1 | Check and confirm that the inverter's power limit or anti-reverse function is off | NA | Power on inverter | Visually | If the inverter has the functions of anti-reverse, over-frequency load reduction, PU curve, and slope loading, turn off these functions as appropriate according to local requirements; If the inverter does not enable the functions of anti-reverse, over-frequency load reduction, PU curve, and slope loading, please proceed to step 2
Step 2 | Check and confirm whether the grid voltage of the inverter is within the selected safety regulations | Multi-meter | Power on inverter | Use a multimeter to measure the grid voltage at the output | If the measured grid voltage is close to the upper limit of the safety regulation range, it may trigger overvoltage reduction, and the inverter safety regulation shall be changed to 50 / 60Hz Default; If it is found that the AC side frequency of the inverter is close to the upper limit of the safety regulation range, it may trigger overvoltage derating or overfrequency derating, and the inverter safety regulation shall be changed to 50 / 60Hz Default; If the measured grid voltage is within the allowable range of safety regulations, please proceed to step 3
Step 3 | Check and confirm that the module parameters are normal | Multi-meter | Shut down the inverter and disconnect the cables between the modules connected to the inverter from both the inverter and the module | Test the parameters of the string, open circuit voltage and short circuit current, and then compare with the parameter information on the label of the panel | If the comparison between the measured value and the parameter on the module label does not meet the module aging rule, it is suspected to be a module-side problem. It is recommended to correct the module until the module parameters meet the requirements; If the comparison between the measured value and the parameter on the module label meets the aging rule of the module, please proceed to step 4;
Step 4 | Check and confirm that the installation environment of the inverter meets the installation requirements of Goodwe User Manual | NA | NA | Check it visually | If the installation environment of the module has a shadow barrier, please adjust it until it meet the requirements of the photovoltaic power plant installation; If the PV Array's inclination and azimuth do not conform to the reasonable range values in the area, please correct the PV Array's installation inclination and azimuth until they meet the reasonable range values in the area; If there is debris or dust on the array's surface, please clean the array's surface until it is clean; If there are hot spots and cracks inside the PV module, please check with professional equipment until the module runs normally If the inverter is installed in a closed environment, the inverter will experience excessive temperature and load reduction, and the installation position needs to be changed until the operation is normal. If the above installation environment does not exist, then go to step 5
Step 5 | Check and confirm that the cable diameter of the inverter connected to the power distribution cabinet meets the requirements | NA | Turn on the inverter and turn on the electrical appliances in the user's home | When the power generation is high at noon, it is recommended that customers turn on the high-power electrical appliances at home to check the inverter power changes | If the power generated by the inverter increases after the high-power electrical appliance is turned on, it proves that the cable diameter of the inverter connected to the power distribution cabinet of the power grid is too thin, and the power transmission capacity is limited. ; If there is no significant increase or change in the power generation of the inverter after the high-power electrical appliance is turned on, please contact Goodwe service team to confirm the solution

## Terminal burnt
Symptom | Terminal burnt
Fault Description | AC or DC terminals burnt
No. | Description of Troubleshooting | Tools | Preparation before checking | Detection method | Judgment and Solution
Step 1 | Check and confirm whether the customer is using our standard DC connector(including battery connector) | NA | Shut off the inverter | Visually | If the DC terminal burnt because the terminal used by the customer is not the standard DC terminal supplied by Goodwe, the warranty is void in this condition. If the inverter uses GoodWe standard DC terminals, please go to step 2
Step 2 | Check and confirm that the DC terminals of the inverter meet the crimp requirements | NA | Shut off the inverter | Visually | If the DC terminal burnt because of a poor DC terminal crimping condition and does not meet the installation requirements of the user manual, the warranty is void in this kind of situation. If the DC terminals of the inverter are well crimped and meet the installation requirements of the user manual, please go to step 3
Step 3 | Check and confirm that there is no reverse connection between the positive and negative poles of each DC string | Multimeter | Shut off the inverter,Disconnect all strings from the inverter | Use a multimeter to measure the voltage between the positive and negative poles of each string. The multimeter selects the DC voltage range (the voltage range is greater than the open-circuit voltage range of the string). The red test lead is connected to the positive electrode, and the black test lead is connected to the negative electrode. | If there is a reverse connection between the positive and negative poles of any DC string which resulted in the DC terminal burning out, which does not meet the installation requirements of the user manual, the site needs to be rectified until the string positive and negative poles meet the installation requirements. The warranty is void in this condition. If there is no reverse connection between the positive and negative poles of any DC string measured, please go to step 4
Step 4 | Check and confirm that there is no cross wiring between DC strings | NA | Shut off the inverter,Disconnect all strings from the inverter | Use a multimeter to measure the voltage between the positive and negative poles of each string. The multimeter selects the DC voltage range (the voltage range is greater than the open-circuit voltage range of the string). The red test lead is connected to the positive electrode, and the black test lead is connected to the negative electrode. | If the voltage value between the positive and negative poles of any DC string is abnormal (much smaller than the open-circuit voltage of the string), there is a cross-wiring problem between the DC strings. Please rectify on site until each DC string works normally ; If the voltage between the positive and negative poles of each DC string is normal, please go to step 5
Step 5 | Check and confirm that the AC terminals of the inverter have no bad crimping | NA | Shut off the inverter,shut down the AC switch | Pull the AC cable to the outside to check whether the AC terminal is crimped in place. | If the inverter has poor crimping of the AC terminals and causes the AC terminals to burn out, it does not meet the installation requirements of the user manual, which is makes the warranty void. If the inverter's AC terminals are crimped, please go to step 6
Step 6 | Check and confirm that the material of inverter AC cable meets the requirements of the user manual | NA | Shut off the inverter,,shut down the AC switch | Visually | "If the inverter's AC cable is made of aluminum and copper-aluminum alloy terminals are not used,which leads the AC terminals burned out, this condition does not meet the installation requirements of the user manual and is beyond the warranty scope; If the inverter AC cable is made of aluminum and copper-aluminum alloy terminals are used, the requirements of the user manual are met. Go to step 7; If the material of the inverter AC cable is copper wire, it meets the requirements of the user manual, please go to step 7
Step 7 | Check and confirm that the diameter of the AC cable of the inverter meets the requirements of the user manual | Micrometer | Shut off the inverter,,shut down the AC switch | Measure the actual cable outer diameter and inner diameter with a micrometer | If the diameter of the AC cable is smaller than that required in the user manual,which leads the AC terminals to be burned out, it does not meet the installation requirements of the user manual and the warranty is void; If the diameter of the AC cable is greater than or equal to the wire diameter required in the user manual, it meets the requirements of the user manual, please go to step 8
Step 8 | Check and confirm whether the inverter has been struck by lightning | Screwdriver, multimeter | Shut off the inverter, and disconnect all the wirings on both DC and AC sides from the inverter | Open the inverter cover and check the status of the SPD | If the inverter lightning protection module is damaged, it means that the inverter has been struck by lightning, and the lightning strike is beyond the warranty scope; If the inverter lightning protection module does not have any sign of damage, it means that the inverter has not been struck by lightning. Please contact Goodwe service team to confirm the solution.

## Water inside the inverter
Symptom | Water inside of inverter
Fault Description | Water enters inverter, causing the inverter fails to work properly or affecting some functions
No. | Description of Troubleshooting | Tools | Preparation | Detection method | Judgment and Solution
Step 1 | Check and confirm that the sealing condition of inverter external is good | NA | NA | Check whether all the used terminals are well connected and whether the screws are tight; check whether all unused terminals are well blocked; check whether the external sealing screws are tight | If the external sealing of the inverter is not good, it is considered that the installation does not meet the requirements of the user manual*, which resulted in the inverter's IP65 cannot be achieved,warranty void in this condition; If the external sealing of the inverter is good, go to step 2.
Step 2 | Check that there is no internal water in the inverter | Screwdriver | Shut down the inverter | Open the cover of inverter | If there is stagnant water in the inverter, it is judged as water inside inverter, please contact Goodwe service team to confirm the solution* If there is no water in the inverter, please go to step 3
Step 3 | Check and confirm that there is no moisture condensation inside the inverter | Screwdriver | Shut down the inverter | Open the cover of inverter | If there is condensation water inside the inverter, which affects the normal function, please contact Goodwe service team for the solution*; If there is condensation water inside the inverter, and it will not affect the normal function and use.It can be eliminated by itself under good weather conditions.

## Inverter cannot start up
Symptom | Inverter LED are off, cannot power on
Fault Description | Inverter cannot power on
No. | Description of Troubleshooting | Tools | Preparation | Detection method | Judgment and Solution
Step 1 | If the inverter just conenct to PV but cannot power on,check and confirm that the inverter DC switch is turned on | NA | NA | Check the status of the DC switch | If the inverter DC switch is in the "OFF" state, please turn on the DC switch and observe whether LEDs of the inverter are on; If the inverter DC switch is already “On”, go to step 2.
Step 2 | If the inverter just conenct to PV but cannot power on, check and confirm that the string voltage on the DC side of the inverter reaches the minimum starting voltage of the inverter | Multimeter | Shut down the inverter and disconnect all DC strings from the inverter | Use a multimeter to measure the open circuit voltage between the positive and negative poles of each DC string | If the string voltage on the DC side of the inverter is less than the minimum starting voltage of the inverter, check the module configuration and DC side wiring until the string voltage on the DC side reaches the minimum starting voltage of the inverter.If the string voltage on the DC side of the inverter is greater than or equal to the minimum start-up voltage of the inverter, and still cannot start after waiting for 5-10mins, go to step 3.
Step 3 | If the inverter just conenct to PV but cannot power on, check and confirm that there is no reverse connection between the positive and negative poles of each DC string | Multimeter | Shut down the inverter and disconnect all strings from the inverter | Use a multimeter to measure the voltage between the positive and negative poles of each string. The multimeter selects the DC voltage range (the voltage range is greater than the open-circuit voltage range of the string). The red test lead is connected to the positive electrode, and the black test lead is connected to the negative electrode. | If there is a reverse connection between the positive and negative poles of any DC string to be measured, the site needs to be rectified until the positive and negative strings of the string meet the installation requirements; If there is no reverse connection between the positive and negative poles of any DC string measured, please go to step 4.
Step 4 | If the inverter is only connected to the battery and cannot be turned on,check the battery voltage | Multimeter | Power on inverter | Measure the output voltage of the battery | The battery voltage must be higher than a certain value before the inverter can start;
Step 5 | If the inverter is only connected to the AC and cannot be turned on, check the grid voltage | Multimeter | Power on inverter | Measure voltage at ongrid terminal | If there is no voltage on the on-grid end of the inverter, check the cables on the on-grid end. If there is a problem with the cable, rectify the cable until there is voltage; if the voltage on the on-grid end of the inverter is normal and cannot be turned on, contact Goodwe service team.

## Utility Lost
Symptom | Utility Loss (Grid Loss or Error code 23)
Fault Description | The inverter detects no AC voltage ,the voltage is lower than the safety low voltage.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Confirm that other electrical equipment under the same grid connection works normally, and the mains power supply is normal | NA | NA | Visually | If other electrical equipment under the same grid does not work properly, it is determined that the power grid is abnormal. Please contact the electrician or local power grid company to troubleshoot the power grid until the power grid returns to normal; If other electrical equipment under the same grid connection works normally, please go to step 2
Step 2 | Confirm that the upper AC switch of the inverter is closed and intact | Multimeter | NA | Visual inspection; Multimeter measures the voltage at the upper and lower ends of the AC switch | If the upper AC switch of the inverter is open, please close the switch; If the upper AC switch of the inverter is in the closed state, measure the voltage value at the upper and lower ends of the AC switch. If the measured upper and lower voltage values of the switch are different, the AC switch is judged to be damaged and the upper AC switch of the inverter needs to be replaced. If the inverter's upper-level AC switch is intact, please go to step 3
Step 3 | Confirm the AC wiring is good | NA | Power off the inverter and turn off the AC side switch | Pull the AC cable outward manually | If the inverter has poor AC termination wiring, it needs to be rectified until the AC side wiring is good; If the inverter AC wiring is good, go to step 4.
Step 4 | Confirm that the overvoltage and undervoltage protector is not working | NA | NA | Visually | If the over / undervoltage protector is disconnected, it needs to be removed; Pay attention to the installation direction of the overvoltage and undervoltage protectors. If the connection is reversed, the overvoltage and undervoltage will not work (the upper end of the overvoltage and undervoltage must be connected to the power grid) If the over / under voltage protector does not work, please go to step 5
Step 5 | Confirm that the inside of the inverter is intact | Multimeter | Shut down AC，DC | Multimeter resistance measurement of impedance between live and neutral wires of the inverter | If the measured impedance between the live and neutral wires on the AC side is much less than 200KΩ, it means that there is internal continuity between the live and neutral wires, and it is recommended to contact Goodwe headquarters to confirm the solution; If the measured impedance between the live and neutral wires on the AC side is greater than 200KΩ, it indicates that the live and neutral wires of the inverter are not connected. please go to step 6.
Step 6 | Confirm the neutral and ground wires are well wired | Multimeter | NA | Use a multimeter to measure the voltage between the neutral and ground of the inverter | If the measured voltage between neutral and ground is greater than 10V, it indicates that the site has poor grounding. It is recommended to rectify until the voltage between neutral and ground is 10V or less; If the measured voltage between neutral and ground is less than or equal to 10V, please go to step 7.
Step 7 | Confirm that the AC side wiring meets the requirements | Multimeter | NA | Measure the AC side wiring of the inverter with a multimeter | If it is found that the neutral line of the inverter AC and ground are reversely connected, it is recommended to rectify until the neutral and ground lines are in the correct position; If it is found that there is a reverse connection between the neutral line and live line on the AC side of the inverter, it is recommended to rectify until the neutral line and live line are in the correct position; If the inspection shows that the AC side wiring is in the correct position, please contact GoodWe service team for solution.

## ISO failure
Symptom | The inverter screen shows "ISO Failure" or "The panel has low insulation resistance to ground" or "Error code 14"
Fault Description | Suspected component problems(the insulation resistance to ground is less than 100KΩ)
No. | Description of Troubleshooting | Tools | Preparation | Detection method | Judgment and Solution
Step 1 | confirm the panel module type, and confirm whether it is a crystalline silicon module or a thin film module | NA | NA | Visually | If it is a crystalline silicon module, go to step 2; For thin film modules, please contact Goodwe service team for confirmation
Step 2 | Check and confirm whether the frame of the component and the metal bracket are well grounded (whether the grounding hole of the module frame is grounded) | Multimeter | NA | Use a multimeter to measure the resistance between the module frame and the metal bracket (grounded) | If the ground resistance is less than or equal to 10 ohms, it is determined that the ground is good, please go to step 3; If the grounding resistance is greater than 10 ohms, it is determined to be bad grounding. Please correct the grounding until the resistance is less than or equal to 10 ohms. If the problem persists, go to step 3.
Step 3 | By connecting only one string at a time, it is determined whether the fault is caused by one or more strings. | NA | Shut down the inverter; unplug all strings from the inverter | Connect only one group of strings at a time, and then turn on the inverter to see if it is successfully connected to the grid. Connect and test all strings in this way. | When each group of strings is connected in turn, the inverter displays ISO failure, it is determined to be an inverter problem, please contact Goodwe service team to confirm the solution; When each group of strings is connected in sequence, the inverter works normally, but when all strings are connected, the inverter reports ISO failure. Please contact Goodwe service team to confirm the solution; When each group of strings is connected in turn, some strings show ISO failure, but the other strings are working normally, please go to step 4
Step 4 | Check and confirm that PV string has good impedance to ground | Impedance meter | Shut down the inverter and disconnect the cables between the inverter and the module from both the inverter and the module | Connect the positive terminal of the impedance meter to either end of the cable and ground the negative terminal to read the impedance value. | If the impedance value is greater than or equal to 10 ohms, it is judged that the cable is well insulated, please go to step 5; If the impedance value is less than 10 ohms, it is determined that the cable is not well insulated. Please replace or repair the cable and measure again until the impedance value is greater than or equal to 10 ohms, and then go to step 5. You can use the multimeter DC gear to test the positive and negative voltages of the components respectively. If the positive or negative DC voltage is a fixed value, it indicates that there is a problem with the string. If the positive or negative DC voltage is a constant change during measurement A small value indicates that the string is normal. [This solution can be used as an auxiliary reference]
Step 5 | Check and confirm that the surface of the module cable is good | NA | NA | Visula inspection | If damaged, please replace the cable; if there is no problem, please go to step 6
Step 6 | Check and confirm that the AC side is well grounded | Multimeter | Shut down the inverter | Measure whether the N and ground wires in the AC terminal are well connected | If the impedance of the N and ground wires in the AC terminal is less than 10 ohms, it is determined to be well grounded. If it is greater than or equal to 10 ohms, check the ground wire on the AC side until the measured value above is less than 10 ohms. If the fault continues Unable to resolve, please contact Goodwe service team to confirm the solution
Step 7 | If it is a high-voltage battery, the positive and negative electrodes of the battery have a good impedance to ground (low-voltage batteries ignore this step) | Multimeter | Power on inverter | Using a multimeter to measure the impedance of the positive and negative poles of the power line of the high-voltage battery to ground | If the impedance value is greater than or equal to 1M ohm, the cable insulation is determined to be good; If the impedance value is less than 1M ohm, it is judged that the cable insulation is poor, please replace or repair the cable and measure again until the impedance value is greater than or equal to 500K ohm;

## Ground I
Symptom | Error "Ground I" or "Excessive leakage current" "Error code 22/32"
Fault Description | Detected leakage current is large
No. | Description of Troubleshooting | Tools | Preparation | Detection method | Judgment and Solution
Step 1 | Confirm that the error is not related to the weather | NA | NA | Visual inspection: observe the working condition of the inverter on a sunny day | If the fault occurs in rainy weather or morning/evening only, it may be due to the high humidity environment. The leakage current of the solar panels increases due to the increase in the parasitic capacitance to the ground. After the weather is clear, the error can be automatically eliminated and the normal operation can be resumed; If the fault occurs on a sunny day, go to step 2
Step 2 | Confirm that AC and DC has good grounding | Multimeter | NA | Visual inspection: Observe module grounding Use a multimeter to measure the impedance between the AC-side ground wire and the ground copper bar of the grid-tied point | If the modules are well grounded, and the impedance between the module frame and the metal bracket (grounded) is greater than 10 ohms, the module is judged to be poorly grounded. Please correct the DC side grounding until the resistance is less than or equal to 10 ohms; If the impedance between the AC-side ground wire and the grounding copper bar of the grid-tied point is greater than 10 ohms, it is determined that the AC grounding is poor, please correct the grounding until the resistance is less than or equal to 10 ohms; If the DC component is well grounded and the AC side is well grounded, go to step 3.
Step 3 | Confirm the string cables are well insulated | / | Shut down the inverter | Plug and unplug each string in turn | If the inverter displays a fault when each group of strings is connected in turn, please contact Goodwe headquarters to confirm the solution; If each group of strings is connected in sequence, the inverter works normally, but when all strings are connected, the inverter reports a fault, please contact Goodwe headquarters to confirm the solution; If each group of strings is connected in sequence, some of the strings are faulty, but the other strings are working normally. Please check the cables of these abnormal strings until the strings can work normally.
Step 4 | The positive and negative electrodes of the high-voltage battery have good impedance to ground | Multimeter | NA | Using a multimeter to measure the impedance of the positive and negative poles of the power line of the high-voltage battery to ground | If the impedance value is greater than or equal to 1 ohm, the cable insulation is determined to be good; If the impedance value is less than 1 ohm, it is judged that the cable insulation is poor, please replace or repair the cable and measure again until the impedance value is greater than or equal to 1 ohm
Step 5 | Confirm that the insulation of the high-voltage battery cable is good | NA | NA | Disconnect the battery, the inverter is only connected to the PV and grid, to see if it can be connected to the grid | If it can be connected to the grid normally, it means that the insulation of the battery cable is abnormal. Check and correct the battery cable until it is normal.

## DC Injection High
Symtom | Error“DC Injection Failure”or“Error code 29”
Fault Description | The DC injection of the inverter is too high during output.
No. | Description of Troubleshooting | Tools | Preparation | Detection method | Judgment and Solution
Step 1 | South Africa and Italy have high requirements for DC injection, and may need to modify DC injection parameters remotely | Laptop | NA | Upgrade the latest DSP version | If the inverter runs normally after upgrading the DSP*, you do not need to continue processing If the inverter still reports an error after upgrading the DSP, please contact Goodwe service team for further sulotion;

## Relay Check
Symptom | Relay-Check Failure (Error code 07)
Fault Description | The inverter detected a fault in the relay.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Confirm if the neutral and ground wires are well wired at the on-grid side | Multimeter | Power off AC，DC | Use the multimeter to measure the voltage between the neutral and ground of the inverter on-grid side | If the measured voltage between neutral and ground at on-grid side is greater than 10V, it indicates that the site has poor grounding. It is recommended to rectify until the voltage between neutral and ground is 10V or less; If the measured voltage between neutral and ground is less than or equal to 10V, please go to step 2
Step 2 | Confirm if the neutral and ground wires are well wired at the backup side | Multimeter | Power off AC，DC | Use the multimeter to measure the resistance between the neutral and ground of the backup side | Resistance of N to PE at backup side shoule be less than 10 Ω,if not, modify the grounding until the resistance is less than 10Ω;If this step no problem please go to step 3.
Step 3 | Check and confirm if the inverter can normal work after restart | NA | NA | Restart the inverter | If the inverter can be started normally after restarting, it can be judged that the error is caused by the disturb of the AC voltage , no need to deal. If the inverter still cannot be started after restarting, please contact GoodWe service team for solution.

## VAC Failure
Symptom | Vac Failure (Error code 15)
Fault Description | The inverter detected that the grid voltage exceeded the safety requirements.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check and confirm that the AC voltage is within the range of the safety requirement | NA | NA | NA | Read from PVmaster if the AC voltage is out of the range of the the safety requirement, it must be the grid problem instead of the inverter problem, can try to change the safety to 50hz grid default/60hz grid default; If the AC voltage is under the range of the safety requirement, go to step 2.
Step 2 | Check and confirm the AC wiring is good at on-grid side | NA | Shut down the AC switch and power off the inverter | Pull the AC cable outward manually | If the inverter has poor AC termination wiring, it needs to be rectified until the AC side wiring is good; If the inverter AC wiring is good, please go to step 3
Step 3 | Confirm the AC cables at on-grid side is not connect to backup side | Multimeter | NA | NA | Check the AC cables at on-grid side and backup side are correct, can measure by multimeter.
Step 4 | Check and confirm the neutral and ground wires are well wired at the on-grid side | Multimeter | NA | Use the multimeter to measure the voltage between the neutral and ground of the inverter at the on-grid side | If the measured voltage between neutral and ground is greater than 10V, it indicates that the site has poor grounding. It is recommended to rectify until the voltage between neutral and ground is 10V or less; If the measured voltage between neutral and ground is less than or equal to 10V, please go to step 5
Step 5 | Check and confirm the AC Voltage sampling is normal | Multimeter,computer | NA | Use the multimeter to measure the AC voltage, use the calibration tool to calibrate the inverter AC voltage | If the AC voltage show on PVmaster is different with the measured value, please use the calibration tool to calibrate the ac voltage; If calibration failed for several times(more than three times), please go to step 6 If the AC voltage show on the PVmaster is same with the measured value, please go to step 6
Step 6 | Check and confirm that the control board is normal（only for ES，ET） | Screw driver, spare control board | NA | Change the control board | If the inverter work normal after replacing the spare control board, no need to deal more; If the inverter keep giving VAC error after replacing the spare control board, please contact GoodWe service for solution.

## FAC
Symptom | FAC Failure(Error code 03)
Fault Description | The inverter has detected that the frequency of the power grid exceeds the range permitted by the machine's safety regulations.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check and confirm that the AC frequency is satisfied with the local safety requirement | NA | NA | NA | If the AC frequency is different with the local safety requirement, please re-select the suitable safety according to the local requirement; If the AC frequency is same with the local safety requirement, please go to step 2
Step 2 | Check and confirm the how often the error is | NA | NA | NA | If error FAC happens occasionally, it may be caused by the instantaneous grid frequency change, inverter will automatically return to normal, no need to dealm with; If error FAC happens often and can not recover by itself, please go to step 3
Step 3 | Confirm that other electrical equipment under the same grid connection works normally, and confirm the grid power supply is normal | NA | NA | NA | If other electrical equipment under the same grid does not work properly, it is determined that the power grid is abnormal. Please contact the electrician or local power grid company to troubleshoot the power grid until the power grid returns to normal; If other electrical equipment under the same grid connection works normally, please go to step 4
Step 4 | Check and confirm the neutral and ground wires are well wired at the on-grid side | Multimeter | NA | Use the multimeter to measure the voltage between the neutral and ground of the inverter at the on-grid side | If the measured voltage between neutral and ground is greater than 10V, it indicates that the site has poor grounding. It is recommended to rectify until the voltage between neutral and ground is 10V or less; If the measured voltage between neutral and ground is less than or equal to 10V, please go to step 5
Step 5 | Check the real frequency from PVmaster when the inverter gives the error | NA | NA | NA | If the frequency shown on the PVmaster is out of the range of the safety requirement, inverter will automatically return to normal, no need to deal; if the frequency shown on the PVmaster is under the range of the safety, please go to step 6
Step 6 | Check and confirm that the control board is normal（only for ES，ET） | screw driver,spare control board | NA | Replace the control board | If the inverter works normal after replacing the spare control board, no need to deal more*; If the inverter keep giving this error after replacing the spare control board, please contact GoodWe service team for solution.

## PV over voltage
Symptom | Error“PV over voltage”or "Display over voltage" Error Code：17
Fault Description | The input voltage of the DC string exceeds the allowable range of the inverter(for hybrid inverters with Low voltage battery)
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Jugdment and solution
Step1 | Check if the voltage of each string from PV side meets the requiremnts of the inverter. | Multimeter | Power off the inverter; Disconnect all the PV strings from the inverter. | Use multimeter to check the open circuit voltage between PV+ and PV- of each string; Calculate the maximum voltage of the PV string based on the actual PV configuration and local meteorological record. | If the max PV Voc are out of inverter DC voltage range ,please reduce the pv panel amount till the Voc is under the requirement. If the Voc is under the requirement, please go to step 2
Step2 | Check and confirm if the voltage of PV side is same with the voltage on PV master. | Multimeter | NA | Use multimeter to check the voltage of each string from PV side and compare it with the voltage on LCD to comfirm whether they are same or not. | If the PV Voc are not same with the voltage on PV master, it is the data sampling problem, it need to be calibrated with calibration tool*; If it still not work, it has to be replaced with the control board(for ES model only)*;If still cannot solve please contact Goodwe service team for solution.
返回首页

## DC over voltage
Symptom | Error“DC over voltage”or Error Code：17
Fault Description | The input voltage of the DC string exceeds the allowable range of the inverter(For hybrid inverters with High voltage battery)
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Jugdment and solution
Step1 | Check if the voltage of each string from PV side meets the requiremnts of the inverter. | Multimeter | Power off the inverter; Disconnect all the PV strings from the inverter. | Using multimeter to check the open circuit voltage between PV+ and PV- of each string; Calculate the maximum voltage of the PV string based on the actual PV configuration and local meteorological record. | If the max PV Voc are out of inverter DC voltage range ,please reduce the pv panel amount till the Voc is under the requirement. If the Voc is under the requirement, please go to step 2
Step2 | Check and confirm if the voltage of each string from PV side are same with the voltage on PV master. | Multimeter | NA | Use multimeter to check the voltage of each string from PV side and compare it with the voltage on PVmaster to comfirm whether they are same or not. | If the PV Voc are not same with the voltage on PVmaster,it is the data sampling problem, it need to be calibrated with calibration tool; If it still not work, it has to be replaced with the control board(for ET only)*;
Step3 | Check and confirm if the voltage of battery meets the requirements of inverter. | Multimeter | NA | Use multimeter to check the battery voltage; | If the max battery voltage is out of inverter DC voltage range ,please reduce the number of the batteies or contact your battery vendor. If the voltage is under the requirement, please go to step 4.
Step4 | Check and confirm if the voltage of battery are same with the voltage on PV master. | Multimeter |  | Use multimeter to check the voltage of battery side and compare it with the voltage on PVmaster to comfirm whether they are same or not. | If the battery Voc are not same with the voltage on PVmaster,it is the data sampling problem, it need to be calibrated with calibration tool; If it still not work, it has to be replaced with the control board(for ET only)*;If still not work please contact Goodwe service team.

## Over temperature
Symptom | Over temperature or Error Code 19
Fault Description | Inverter over temperature protection, the internal temperature of the inverter reaches the inverter over temperature protection point.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Jugdment and solution
Step1 | Check and confirm the inverter installation meets the user manual requirements | NA | NA | Visually | If the inverter installation doesn't meet the user manual requirements, please reform the installation till meeting the user manual requirements If the inverter installation meets the user manual requirements, please go to step 2
Step2 | Check and confirm the temperature surrounding the inverter | Thermometer | NA | Visually | If the temperature surrounding the inverter is over 45℃，then it is the problem of over temperature of the working environment ,please cool down the working temperature till lower than 45℃. If the temperature surrounding the inverter is below 45℃, please go to step 3
Step3 | Check and confirm the inverter is normal | NA |  | Power off the inverter for 15mins then restart the inverter | If the inverter could work normally after restarting, then it is the problem of too high temperature. If the inverter couldn't work normally after restarting, then please contact GoodWe service team for solution.
返回首页

## EEP Rom RW Failure
Symptom | Error "EEP Rom RW Failure" or "Storage and read exception" "Error code 02"
Fault Description | Control board storage chip read and write failure
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check and confirm the software version of the inverter | Laptop | NA | Upgrade to the latest DSP version | If the inverter runs normally after upgrading the DSP, you do not need to continue processing If the machine still reports an error after upgrading the DSP,please go to step 2;
Step 2 | Check and confirm that the control board is normal（for ES，ET only） | Screwdriver, control board spare parts | NA | Replace the control board | If the inverter works normally after replacing the control board*, there is no need to continue processing; If the inverter does not work properly after replacing the control board,please contact GoodWe service team for solution.

## SPI SCI
Symptom | Error "SPI Failure" or "Internal communication failure" "Error code 01"
Fault Description | Internal communication failure or failure of reading the master and slave chips of the control board
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check and confirm the software version of the inverter | Laptop | NA | Upgrade to the latest version | If the inverter runs normally after upgrading the DSP, you do not need to continue processing; If the inverter still reports an error after upgrading the DSP,please go to step 2;
Step 2 | Check and confirm that the control board is normal (for ES ET only) | Screwdriver, control board spare parts | NA | Replace the control board | If the inverter works normally after replacing the control board*, there is no need to continue processing; If the inverter does not work properly after replacing the control board,please contact GoodWe service team for solution.

## DC Bus High
Symptom | Error "DC Bus High" or "Error code 21"
Fault Description | The DC bus voltage inside the device is too high
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check and confirm that the inverter is normal | Smart Phone/PVamster | NA | Restart the inverter | If the inverter returns to normal after restarting the inverter, the problem is solved; If after restarting the inverter, it still reports an error and cannot work normally, please proceed to step 2
Step 2 | Check and confirm that the open circuit voltage of each string on the actual PV side meets the requirements of the inverter user manual | Multimeter | Power off the inverter; unplug all strings from the inverter side | Use a multimeter to measure the open circuit voltage between each string PV + and PV-; | If the actual open circuit voltage of the string exceeds the allowable range of the inverter, it is determined that the string is overmatched. Please correct the PV string until the open circuit voltage of all strings meets the requirements. If the actual open circuit voltage of the string is within the allowable range of the inverter, please proceed to step 3.
Step 3 | Check and confirm that the theoretical open circuit voltage meets the requirements of the inverter user manual | NA | NA | Calculate the maximum open circuit voltage of the string according to the actual component configuration information on site and the local historical environmental conditions. | If the calculated maximum open circuit voltage of the string exceeds the allowable range of the inverter, it is determined that the string is overmatched. Please correct the PV string until all the string open circuit voltages meet the requirements. If the calculated maximum open circuit voltage of the string is within the allowable range of the inverter, go to step 4.
Step 4 | Check and confirm that the PV string has good impedance to ground | Impedance meter | Power off the inverter, and disconnect the cables connecting the inverter and components from both the inverter and component ends. | Connect the positive pole of the impedance meter to either end of the cable and ground the negative pole to read the impedance value. | Measure the impedance of PV positive and negative to the ground (inverter cover), should be greater than or equal to 30K ohms, if less than 30k ohms, rectify the insulation of the PV string to ground until it meets the requirements, or refer to the ISO failure solution; if it is within the range, proceed to the next step ;
Step 5 | Check and confirm the software version of the inverter | NA | NA | View the current software version information of the inverter | If the software version of the inverter is not the latest version, please upgrade to the latest version; If the software version of the inverter is the latest version, please go to step 6.
Step 6 | Check and confirm that the control board is normal（for ES，ET only） | Screwdriver, control board spare parts | NA | Replace the control board | If the inverter works normally after replacing the control board*, there is no need to continue processing; If the inverter does not work properly after replacing the control board,please contact GoodWe service team for solution.

## AC HCT failure
Symptom | Error“AC HCT failure”or“Error code 31”
Fault Description | AC output current sensor failure
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check and confirm the software version of the inverter | NA | NA | View the current software version information of the inverter | If the DSP software version of the inverter is not the latest version, please upgrade to the latest version*; If the software version of the inverter is the latest version, please proceed to step 2.
Step 2 | The cable between the control board and the output board to confirm whether it is loose（for ES，ET only） | Screwdriver | Power off inverter | Replug the cable between the control board and the output board to confirm whether it is loose. | If the cable connection between the control board and the output board is abnormal, correct the cable until the cable connection is normal*. If the cable connection between the control board and the output board is normal, please go to step 3
Step 3 | Check and confirm that the control board is normal（for ES，ET only） | Screwdriver, control board spare parts | NA | Replace the control board | If the inverter works normally after replacing the control board*, there is no need to continue processing; If the inverter does not work properly after replacing the control board,please contact GoodWe service team for solution.

## All LEDs on
Symptom | All LED ON
Fault Description | The control board controls the indicator abnormally.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Confirm that the the cable attached to the surface of the indicator is well plugged. | Screwdriver | Power off the inverter | Replug the cable and check whether it is loose. | If the wiring is abnormal, please correct the wiring until the wiring is normal*, If the cable connection is normal, go to step 2.
Step 2 | Check and confirm the inverter's ARM and DSP software. | NA | NA | View the current software version information of the inverter | If the software version of the inverter is not the latest version, please upgrade to the latest version*; If the software version of the inverter is the latest version, please proceed to step 3.
Step 3 | Check and confirm that the control board is normal.（for ES，ET only） | Screwdriver, control board spare parts | NA | Replace the control board | If the inverter works normally after replacing the control board*, there is no need to continue processing; If the inverter does not work properly after replacing the control board,please contact GoodWe service team for solution.

## All LEDs off
Symptom | All LED OFF
Fault Description | The control board controls the indicator abnormally.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check if Solar WIFI has hot spots. | Smart Phone |  | Power on inverter | If the inverter can be turned on normally, and there is a hot spotof Solar WIFI, the inverter is normal; if the inverter can be turned on but there is no hot spot, then go to step 2; if it cannot be turned on, refer to the check solution of problem inverter cannot start;
Step 2 | Confirm that the the cable attached to the surface of the indicator is well plugged. | Screwdriver | Power off the inverter | Replug the cable and check whether it is loose. | If the wiring is abnormal, please correct the wiring until the wiring is normal*, If the cable connection is normal, go to step 3.
Step 3 | Check and confirm whether the inverter's ARM and DSP software has failed to be upgraded. | NA | NA | View the current software version information of the inverter | If the software version of the inverter is not the latest version, please upgrade to the latest version*; If the software version of the inverter is the latest version, please go to step 4.
Step 4 | Replace the indicator sticker. | Spare stickers | NA | Power on inverter | Turn on the inverter after replacing the sticker*. If the indicator is all on, it is the reason for the sticker; if the indicator is still off, go to step 5.
Step 5 | Check and confirm that the control board is normal（for ES，ET only） | Screwdriver, control board spare parts | NA | Replace the control board | If the inverter works normally after replacing the control board*, there is no need to continue processing; If the inverter does not work properly after replacing the control board,please contact GoodWe service team for solution.

## Waiting
Symptom | "Waiting" "Waiting for Power Generation"
Fault Description | The PV voltage reaches the starting voltage, but not the inverter power generation voltage.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Make sure that the storage inverter is connected to PV and AC or battery and AC or all three(PV,battery and AC). | NA | NA | NA | The inverter must be connected to at least two power sources to connect to grid.
Step 2 | Check and confirm that the currently selected safety regulations of the inverter meet the requirements of the local power grid. | NA | NA | Visually | If the selected safety regulations are inconsistent with the requirements of the local power grid, it is necessary to re-select the appropriate safety regulations according to the actual situation; If the selected safety regulations meet the requirements of the local power grid, please proceed to step 3;
Step 3 | Check and confirm that the string voltage reaches the minimum starting voltage of the machine. | NA | NA | Check the PV voltage displayed on PVmaster. | If the voltage of any string does not reach the minimum starting voltage of the inverter, the inverter should be in Waiting state until the string voltage rises to meet the minimum starting voltage of the inverter; If the voltage of each string reaches the minimum starting voltage of the inverter, please proceed to step 4;
Step 4 | Check and confirm the warning code when the inverter reports an error. | NA | NA | Check the warning code when the inverter reports an error on the PVmaster. See the warning code when the inverter reports an error from the monitoring data. | If there is a warning code when the inverter reports an error,please contact GoodWe service team for solution.
Step 5 | DRED (Australia), remote shutdown (EU)function caused the inverter in waiting mode. | NA | Power on inverter | Visually | Modify 50Hz to confirm whether it is normal. If it becomes normal, add DRED terminal (15K resistance) (Australian inverter) or remote shutdown terminal (European inverter), if there is no this ternimal please contact Goodwe service team for help.
Step 6 | Inverter reason | NA | NA | NA | If the above 5 steps can not be solved, please contact GoodWe service team for solution. | 返回首页

## Reconnecting
Symptom | "Checking" "Reconnecting"
Fault Description | The auto self-test failed, and the self-test is continuously in circulation.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check and confirm that the currently selected safety regulations of the inverter meet the requirements of the local power grid. | NA | NA | Visually | If the selected safety regulations are inconsistent with the requirements of the local power grid, it is necessary to re-select the appropriate safety regulations according to the actual situation; If the selected safety regulations meet the requirements of the local power grid, please proceed to step 2;
Step 2 | Check and confirm that the string voltage reaches the minimum starting voltage of the inverter. | NA | NA | Check the PV voltage displayed on PVmaster. | If the voltage of any string does not reach the minimum starting voltage of the inverter, the machine should be in Waiting state until the string voltage rises to meet the minimum starting voltage of the inverter; If the voltage of each string reaches the minimum starting voltage of the inverter, please proceed to step 3;
Step 3 | Check and confirm that the on-grid and backup side neutral wires and ground wire are both well connected. | Multimeter | NA | Use a multimeter to measure the voltage on the neutral cable of the inverter to ground at on-grid and backup side saperately. | If the voltage between the neutral cable and the ground cable is greater than or equal to 10V, it is determined that the grounding is poor. Please correct the ground until the voltage between the zero line and the ground line is less than 10V If the voltage between the neutral cable and the ground cable is less than 10V, it is determined that the grounding is good, please go to step 4;
Step 4 | Confirm that the AC wiring is ok. | / | Power off the inverter and turn off the AC side switch. | Manually pull the AC cable outward. | If the inverter has poor AC termination wiring, it needs to be rectified until the AC side wiring is good; If the AC side of the inverter is well connected, please go to step 5;
Step 5 | Check and confirm the warning code when the inverter reports an error. | NA | NA | PV master or remotely check the warning code when the inverter reports an error. | If there is a warning code when the machine reports an error, please contact GoodWe service team for solution.

## Noise issue
Symptom | The inverter is noisy.
Fault Description | The sound of the internal inductance of the inverter during power generation.
No. | Description of Troubleshooting | Tools | Preparation before checking | Checking method | Solution
Step 1 | Check and confirm that the currently selected safety regulations of the inverter comply with local grid requirements. | NA | NA | Visually | If the selected safety regulations are inconsistent with the requirements of the local power grid, it is necessary to re-select the appropriate safety regulations according to the actual situation; If the selected safety regulations meet the requirements of the local power grid, please proceed to step 2;
Step 2 | Check and confirm the decibel of the noise on site. | Decibel Meter / Smart phone | NA | Use a decibel meter to measure the actual noise of the on-site inverter, use a smart phone to make video about the noise. | If the actual noise of the inverter is greater than 55dB, please contact GoodWe service team for solution.
*Note:The steps with* needs to confirm and get approval by Goodwe engineers,as it relates to firmware updates,opening cover and replacing spare parts; Otherwise the warranty may void if any installer or electrician did it without Goodwe's permission.